Literature Survey

AI-Driven Sustainable Data Center Cooling Optimization Framework using Digital Twin Technology

| Paper | Method | Dataset Details | Advantages | Limitations | Research Gap |
| --- | --- | --- | --- | --- | --- |
| 1. Optimization Control Strategies and Evaluation Metrics of Cooling Systems in Data Centers: A Review (2024) | • A bibliometric review (CiteSpace) mapping 20 years of data-center cooling research, not a new system. • Compares air cooling (direct/indirect/evaporative) with liquid cooling (cold-plate, immersion, spray). • Reviews three control approaches: PID, Model Predictive Control (MPC), and Reinforcement Learning (RL). • Focuses on cutting cooling energy and improving airflow through better baffle and microchannel designs. • Uses PUE (and its variants), COP, and heat indices as the efficiency metrics. • No digital twin is built; AI is only discussed as a future direction. | • Dataset Name: Bibliometric literature corpus (review, not an ML dataset) • Source: Scopus, Web of Science, IEEE Xplore • URL: Not Reported (subscription databases; no dataset released) • Size: Not Reported • Number of Records: 467 articles (2004-2024) • Number of Features: Bibliographic fields - keywords, citations, co-citation links • Data Type: Text / bibliographic metadata • License: Not Reported • Purpose: Map 20 years of cooling-control and metric research to spot trends • Preprocessing: CiteSpace network building; dedup and filtering (English, engineering) | • Gives a clear, up-to-date map of air vs liquid cooling with real energy/thermal trade-offs. • Compares PID, MPC, and RL so readers see which control gives the biggest savings. • Grounds sustainability in concrete metrics (PUE, COP) and flags their weaknesses. • Large sample and citation analysis make it objective and reproducible. • Highlights high-efficiency options (direct-to-chip, immersion) worth pursuing. | • Being a review, all numbers are borrowed and context-specific, with no original validation. • Digital twins and closed-loop AI control are essentially missing. • English/engineering-only databases likely skip key computer-science DRL work. • Notes PUE's limits but offers no carbon- or water-aware metric. • PID, MPC, and RL are never tested on a common scenario, so the comparison stays qualitative. | • No digital-twin integration - a sensor-synced cooling twin would make the reviewed controls deployable. • No shared benchmark comparing safe RL vs MPC under real thermal limits. • Metrics ignore carbon and water, so multi-objective sustainable optimization is unexplored. • No link to grid carbon or renewables for carbon-aware scheduling. • Waste-heat reuse and hybrid cooling are listed but never jointly optimized. • RL's high data/compute cost points to a need for transfer or federated learning. |
| 2. Analysis of Digital Twin Applications in Energy Efficiency: A Systematic Review (2025) | • A PRISMA systematic review of how digital twins improve energy efficiency across industries. • Searched five databases with Boolean queries on DT plus energy/sustainability/Industry 4.0 terms. • Funnelled about 500,000 records down to 50 final studies. • Identifies the DT stack: simulation, ML/AI, IoT, big data, and cloud. • Groups results by sector (buildings, manufacturing, power, grids) and by benefit type. • Recommends enablers like OPC UA/MQTT middleware, edge computing, and blockchain. | • Dataset Name: PRISMA systematic-review corpus • Source: IEEE Xplore, ScienceDirect, Springer, MDPI, Google Scholar • URL: Not Reported • Size: Not Reported • Number of Records: 50 studies (screened from ~500,000) • Number of Features: Extracted outcomes - energy, cost, emissions, maintenance • Data Type: Text / bibliographic metadata • License: Not Reported • Purpose: Quantify digital-twin energy-efficiency benefits across industries • Preprocessing: PRISMA screening, deduplication, PICO eligibility filtering | • Transparent PRISMA method makes it reproducible and low-bias. • Quantifies DT value (energy, cost, emission savings) across many sectors. • Clearly lays out the enabling tech stack and how real-time sync drives savings. • Lists practical deployment tools (middleware, edge, blockchain). • Broad scope reveals transferable DT design patterns. • Catalogs adoption barriers (cost, data quality, cybersecurity) as a risk checklist. | • No original validation; figures are second-hand and inconsistent across studies. • Data-center cooling is completely absent from the reviewed set. • Sector-mixed results hide which DT choices actually cause the gains. • Real-time sync, model drift, and latency are mentioned but never measured. • Cybersecurity risks are named but not quantified or mitigated. | • DT value is unproven for data-center cooling specifically - a clear domain gap. • Surveyed DTs monitor rather than predict; thermal prediction would enable proactive control. • Most DTs are passive shadows, missing safety-aware closed-loop RL/MPC. • Savings aren't tied to grid carbon or renewables, leaving carbon-aware DTs open. • Long-term model drift needs online learning that no study implements. • Control-grade DTs need tested security and fault tolerance. • Evidence is single-site; federated learning could scale DTs across facilities. |
| 3. Digital Twins for Clean Energy Systems: A State-of-the-Art Review of Applications, Integrated Technologies, and Key Challenges (2025) | • State-of-the-art review of digital twins for clean-energy systems (2020-2025), tied to UN SDGs. • Searched nine databases, narrowing 5,912 records to 136 core papers. • Adds keyword co-occurrence analysis to find four research themes. • Maps DT use across eight energy domains (solar, wind, hydrogen, nuclear, etc.). • Catalogs enabling tech: AI/ML, RL, IoT, cloud-edge, MPC, blockchain, and XR. • Frames interoperability, cybersecurity, and scalability as the key challenges. | • Dataset Name: Systematic-review corpus + keyword co-occurrence set • Source: Nine databases (Scopus, WoS, IEEE, ScienceDirect, Scholar, T&F, Wiley, DOAJ, arXiv) • URL: Not Reported • Size: Not Reported • Number of Records: 136 core papers (from 5,912); 1,359 keywords • Number of Features: Bibliometric fields - keywords, clusters, citations • Data Type: Text / bibliographic metadata • License: Not Reported • Purpose: Survey DT applications, technologies, and challenges in clean energy • Preprocessing: Multi-database screening, dedup, keyword co-occurrence thresholding | • Most recent and broadest DT energy review (nine sectors, 136 papers). • Distinguishes true two-way DTs from passive "digital shadows" - key for real cooling twins. • Reports strong DT benefits (energy efficiency, peak-load cuts, early fault forecasting). • Maps the full AI/IoT/cloud/MPC stack and links DTs to sustainability goals. • Turns challenges (ontologies, security, scalability) into concrete design requirements. • Keyword clustering objectively shows active and under-served areas. | • No original implementation; all figures are borrowed and context-specific. • Data-center cooling is out of scope, so no direct guidance for the project. • Some sectors (tidal, solar-thermal) and topics (blockchain/XR) are thinly covered. • Human-in-the-loop behavior is flagged as uncertain but unresolved. • Missing DT ontologies and standards are diagnosed but not solved. • Security and large-scale compute issues stay qualitative. | • No data-center cooling DT - adapting these patterns to server cooling is a clear opening. • Many "DTs" are passive; a real low-latency, two-way cooling twin is rare. • MPC and RL are listed but not fused into a validated safe controller. • Despite SDG framing, carbon- and renewable-aware optimization is missing. • No open DT ontology, so standard data models are needed for BMS/DCIM integration. • High-fidelity twins are heavy; model reduction plus transfer learning would scale them. • Connected DTs need tested security and graceful fault handling. |
| 4. A Scalable Digital Twin Framework for Energy Optimization in Data Centers (2026) | • A digital twin of a small data center combining IoT sensors, cloud (Google Cloud/Kubernetes), and ML. • Streams sensor data at 1 Hz via a Raspberry Pi gateway over MQTT into the cloud. • LSTM networks forecast energy demand at 1-, 6-, and 24-hour horizons. • An Isolation Forest flags anomalies to add fault awareness. • Aims for lower power and better PUE through workload-aware decisions, not direct control. • The twin is data-driven (ML), not a physics/CFD model; cooling is one AC unit. | • Dataset Name: Custom IoT testbed telemetry (not named or released) • Source: Authors' small data-center testbed (2 Dell servers + 1 AC unit) • URL: Not Reported (private) • Size: ~30 days of 1 Hz telemetry • Number of Records: Not Reported (~30 days at 1 Hz sampling) • Number of Features: A few sensor signals - power, temperature, humidity, CPU load • Data Type: Time-series sensor telemetry • License: Not Reported • Purpose: Train the LSTM energy forecaster and Isolation-Forest anomaly detector • Preprocessing: Sensor calibration, MQTT ingestion, resampling, train/test split | • Real-hardware validation makes the ~10% savings credible, not just simulated. • Cheap, reproducible commodity setup usable by small operators. • Cloud-native backend can scale out to more nodes and sensors. • Multi-horizon LSTM gives operators lead time for proactive decisions. • Anomaly detection adds early warning and basic fault tolerance. • Clear PUE/energy focus aligns with sustainability goals. | • Too small - two servers can't reproduce real airflow, hotspots, or hyperscale behavior. • Not a physics twin, so it can't simulate cooling what-ifs or thermal fields. • Open-loop: it forecasts but never actually actuates cooling setpoints. • Only 30 days of data; 24-hour forecast error rises to 14%. • Cloud dependence adds latency and fails during outages. • Only compared to linear regression, not MPC, RL, or transformers. | • Lacks a physics/CFD layer needed for real thermal prediction and what-if analysis. • No validated closed-loop actuation - real-time sync plus safe control is missing. • Only energy/PUE is optimized; carbon, water, and renewables are ignored. • Two-server scale is unproven at hyperscale; transfer/federated learning could help. • Only air cooling; liquid/immersion for dense AI racks is untested. • ML outputs are opaque, so explainability is needed before automated control. • Assumes reliable sensors - needs fault-tolerant, drift-aware estimation. |
| 5. A Digital Twin Framework for Liquid-cooled Supercomputers as Demonstrated at Exascale (2024) | • ExaDigiT, an open-source digital twin for liquid-cooled supercomputers, built from three modules. • The RAPS module turns job scheduling and resource use into time-resolved power demand. • A Modelica model simulates the transient liquid-cooling plant (pumps, heat exchangers, coolant loops). • Explicitly models rectifier/converter losses to estimate power-conversion efficiency. • An Unreal Engine AR module visualizes system state for inspection. • Physics-based only; ML surrogates are proposed as future work, not built. | • Dataset Name: Frontier operational telemetry (6 months) • Source: ORNL Frontier exascale supercomputer • URL: ExaDigiT framework is open-source (code); telemetry itself Not Reported • Size: ~6 months of telemetry • Number of Records: Not Reported • Number of Features: Cooling (~15 s) and power (~1 s) signals - pumps, exchangers, converters • Data Type: Time-series telemetry + physics simulation • License: Open-source framework (code); data license Not Reported • Purpose: Validate the digital twin by replaying real telemetry • Preprocessing: Telemetry replay, time alignment / resampling to model resolution | • First full digital twin validated on a real exascale liquid-cooled system. • Transient Modelica model captures real cooling dynamics over time. • Covers the whole chain - workload, power, cooling, and losses - in one twin. • Open-source, so other facilities can build and reproduce their own twins. • PUE accurate within 1.4%, trustworthy for planning and design studies. • AR visualization makes complex thermal/power state easy to inspect. | • No optimizer or controller - it only models and replays, so saving actions stay manual. • ML is future work, so predictions rely on physics alone. • Validated only on Frontier, so portability to other cooling types is untested. • Replay validation never tests live forward control or extreme events. • High-fidelity Modelica is compute-heavy and needs specialist skill. • Reports few error metrics beyond PUE and efficiency. | • Models but never optimizes - adding safe RL/MPC would make it an active controller. • Validation is offline; live two-way sync with Frontier is still needed. • Heavy simulation calls for ML surrogates to run near real time. • Ignores carbon, renewables, and water despite targeting energy. • Frontier-specific models need transfer learning to reuse elsewhere. • Replays known workloads; forecasting would enable anticipatory cooling. • Assumes healthy hardware - sensor/pump fault modeling would add resilience. |
| 6. Digital Twin-Based Cooling System Optimization for Data Center (2026) | • A digital twin of Frontier's cooling plant to measure the gap between ideal and deployable control. • Models the plant as three parallel subloops with variable-speed pumps. • Uses a fast Modelica surrogate instead of full CFD. • Optimizes with SLSQP to minimize cooling energy under safety limits. • Compares flow-only, joint flow+temperature, and ramp-constrained joint strategies. • Shows co-optimizing supply temperature with flow roughly doubles the savings. | • Dataset Name: Frontier cooling-system data, 2023 (public release) • Source: ORNL Frontier exascale supercomputer • URL: Public ORNL Frontier release (Figshare DOI 10.6084/m9.figshare.24391240) • Size: 1 year • Number of Records: Not Reported (~52,560 at 10-min resolution) • Number of Features: Per-subloop temperatures, flows, and pump power • Data Type: Time-series operational telemetry • License: Open access (public dataset) • Purpose: Calibrate the Modelica twin and evaluate cooling optimization • Preprocessing: Cleaning, ASHRAE Guideline-14 calibration, surrogate fitting | • Rigorous ASHRAE-14 validation on a full year of real data. • Ramp-constrained version gives realistic, deployable 27.8% savings. • Large 20-30% cooling savings from control alone, no new hardware. • Reveals clear levers (excess flow, supply-temperature co-optimization). • Fast surrogate makes year-long, multi-strategy analysis practical. • Grounded in a real exascale plant, so directly relevant to modern facilities. | • Offline and open-loop - savings are computed, not proven in live control. • No ML or adaptation, so it can't handle drift or fouling online. • One site, one year; transferability is unproven. • Reduced-order model may miss transients and heat-exchanger ageing. • Per-subloop optimization may miss the global optimum. • Fixed ASHRAE margins ignore chip-level hotspots and sensor error. | • Offline optimization needs a live twin with real-time sync and safe RL/MPC. • Static model needs hybrid physics+ML with online learning to track drift. • Only energy is minimized; carbon, water, and cost are ignored. • Cooling is optimized alone, not jointly with workload scheduling. • Decoupled subloops suggest coordinated facility-wide control is needed. • Aggressive setpoints need fault-tolerant, uncertainty-aware control. • One loop tested; hybrid and multi-site scaling via transferable twins is open. |
| 7. Machine Learning Guided Cooling System Optimization for Data Center (2026) | • A three-stage physics-guided ML pipeline on Frontier data to find and recover excess cooling energy. • A monotonic LightGBM surrogate predicts cooling power using physics-based features. • Residuals from this baseline reveal "excess" energy by time and by loop. • Small supply-temperature and flow tweaks are tested to cut power safely. • Guardrails keep PUE >= 1 and heat removal >= 97%, plus a reviewer/audit layer. • Aims for safe, conservative setpoint tuning, designed to be MPC-compatible later. | • Dataset Name: Frontier HPC & Facility Data workbook (2023) • Source: ORNL Frontier exascale supercomputer (public release) • URL: Public ORNL Frontier release (Figshare DOI 10.6084/m9.figshare.24391240) • Size: 1 year (2023) • Number of Records: 49,869 timestamps (after cleaning) • Number of Features: Loop temps, flows, waste heat, compute/accessory power, PUE + derived • Data Type: Time-series tabular telemetry • License: Open access (public dataset) • Purpose: Train a LightGBM surrogate to find and recover excess cooling energy • Preprocessing: Cleaning, physics feature engineering, K-means regime labels, 80/20 split | • Accurate, interpretable surrogate with tiny error and an auditable monotonic structure. • Localizes waste to specific months, hours, and loops for targeted action. • Recovers up to 96% of excess with sub-1 C, safe setpoint tweaks. • Lightweight LightGBM needs no CFD and adds reviewer/audit logs. • Finds real savings even in an already efficient (PUE ~1.05) facility. • Physics features and guardrails transfer to other liquid-cooled plants. | • Offline only - savings are estimated by replay, never tested in closed loop. • One site, one year; needs recalibration to generalize. • Very conservative action space, so realized savings are a lower bound. • Modest R2=0.79, and the smallest estimates sit near model noise. • Workload is exogenous; chillers, towers, and heat recovery aren't modeled. • Static surrogate can't forecast load or weather for proactive control. | • Trained once, never updated - a live self-calibrating twin is needed. • Reactive, not predictive; forecasting would enable MPC-style scheduling. • Only energy/cost optimized; carbon, water, and renewables are ignored. • Stops at recommendations - needs a real closed-loop safe controller. • Treats waste heat as loss; reuse, hybrids, and grid interaction are unexplored. • Aggregate, single-site validation lacks per-rack detail and fault handling. • Only feature importance; real explainable AI with uncertainty is needed for trust. |
| 8. Data Center Cooling System Optimization Using Offline Reinforcement Learning (2025) | • Physics-informed offline RL to control air-cooling units (fan speed and valves). • Uses a graph neural network to capture sensor-and-ACU spatial relationships. • Enforces time-reversal symmetry as a physics prior to learn from scarce data. • Optimizes the policy offline with a behavior constraint to stay safe. • Reward balances energy (fan power) against thermal-safety penalties. • Deploys via Modbus every ~5 minutes with periodic retraining. | • Dataset Name: Commercial DC operational logs + testbed logs (not released) • Source: Real commercial data center (China) + authors' 22-server testbed • URL: Not Reported (proprietary) • Size: ~363k samples in total • Number of Records: ~180k (Room A) + ~140k (Room B) + ~43k (testbed) • Number of Features: ~101-108 (production), 105 (testbed) - temps, humidity, ACU states • Data Type: Time-series operational telemetry • License: Proprietary / Not Reported • Purpose: Train the offline-RL policy for air-cooling-unit control • Preprocessing: Export from DC log system, feature extraction, MDP formulation | • Rare real deployment: 14-21% savings over 2000+ hours with no safety violations. • Data-efficient - physics priors let it learn from limited, narrow data. • Jointly controls many ACUs and saves more at higher loads. • Improves temperature uniformity while using less energy. • Learns from real data, avoiding the CFD sim-to-real gap. • Outperforms PID, MPC, and other RL baselines on the testbed. | • Only air-side ACUs - chillers and water-side loops are left uncontrolled. • Training data come only from cautious PID, limiting explored behaviors. • Air-cooled focus, not the liquid/hybrid cooling of modern AI facilities. • The learned latent model is not an interpretable physics twin. • Safety is soft penalties, not hard guarantees, under rare faults. • Largest claims rest on one site with non-randomized comparisons. | • No explicit predictive twin - forecasting would enable anticipatory control. • Only air-side; chiller/liquid/hybrid control is still needed. • Reward ignores carbon, water, and renewables. • No formal safe-RL guarantees or fault-tolerant fallback. • Opaque policy needs explainability to earn operator trust. • Workload is exogenous; joint job+cooling scheduling could save more. • Each site needs its own data - federated/transfer learning would scale it. |
| 9. LC-Opt: Benchmarking Reinforcement Learning and Agentic AI for End-to-End Liquid Cooling Optimization in Data Centers (2025) | • LC-Opt is an RL benchmark built on ORNL's Modelica digital twin of Frontier's cooling system. • Exports the twin as an FMU wrapped in a Gymnasium API for closed-loop RL. • A JSON-based API builds cooling models from towers down to blade-group valves. • Two coupled control problems handle the cooling towers and the blade groups. • Uses independent per-unit agents plus a centralized-action trick to scale. • A multi-head PPO policy sets temperature, flow, and valve splits; policies distil into trees and LLMs. | • Dataset Name: LC-Opt simulation environment (no fixed dataset) • Source: ORNL ExaDigiT Modelica/FMU twin of Frontier • URL: Open-source code (GitHub: HewlettPackard/sustain-lc) • Size: Not Reported (data generated on the fly by simulation) • Number of Records: Not Reported (episodes over 2-day horizons) • Number of Features: Blade-group heat, weather/wet-bulb traces, temps, flows, power • Data Type: Physics-simulation environment (synthetic + exogenous traces) • License: Open-source (released code) • Purpose: Benchmark RL and LLM controllers for liquid cooling • Preprocessing: JSON model config (AutoCSM), FMU export, Gymnasium wrapping | • End-to-end twin from cooling towers down to individual blade-group valves. • Multi-head PPO hits ~95.6% compliance and cuts tower power, even on larger unseen setups. • A heat-recovery unit cuts ~21% tower power and reuses waste heat. • The valve policy sends coolant where the heat is, avoiding wasted cooling. • Distills RL into trees and LLMs for explainable, trustworthy control. • Open, customizable benchmark for testing RL/LLM cooling controllers. | • Simulation only - no real Frontier deployment, so a sim-to-real gap remains. • Full multi-agent coordination fails at scale, forcing independent agents. • The policy under-cools some low-power groups, causing occasional hotspots. • No chip-level detail or hybrid air+liquid cooling. • Tested on few weather/workload traces, so robustness is limited. • LLM explanations are sometimes incomplete and computationally costly. | • Pure simulation - real hardware validation and live twin sync are the key gaps. • Reacts to current traces; forecasting would enable anticipatory control. • Independent agents lack the global coordination needed at ~10^4 blade groups. • Reward centers on power/temperature, not carbon, water, or renewables. • No hard safety guarantees or sensor/actuator fault handling. • Only liquid loops; chip-level, hybrid, and renewable integration are missing. • LLM explanations need to be verified, cheaper, and uncertainty-aware. |
| 10. Dual-Loop Control in DCVerse: Advancing Reliable Deployment of AI in Data Centers via Digital Twins (2026) | • A Dual-Loop Control Framework: a digital twin plus a reservoir of diverse DRL agents. • Policies are trained and pre-tested in the twin, then expert-verified before real use. • Builds a hybrid physics+data twin in EnergyPlus, calibrated to field data. • Keeps offline and online DRL agents (DDPG, SAC, DQN) to pick the best per case. • Models a chilled-water plant plus CRAH units and hot-aisle containment. • Controls chilled-water/CRAH setpoints and fan speeds to cut power within SLA limits. | • Dataset Name: Field data from one real data center (twin calibration) • Source: A real-world data-center cooling system • URL: Not Reported • Size: Not Reported • Number of Records: Not Reported • Number of Features: CRAH return-air temp, chilled-water temps, plant power (validation vars) • Data Type: Field telemetry + EnergyPlus simulation • License: Not Reported • Purpose: Calibrate the twin and train / pre-evaluate the DRL agents • Preprocessing: Data assimilation into twin, geometry reconstruction, calibration | • Pre-testing in the twin plus expert sign-off makes DRL safe for critical sites. • Physics-informed twin cuts the real-world data needed to train. • A pool of agents lets operators match the policy to conditions. • ~4% savings with full SLA compliance - efficiency without risk. • Inspecting agents in the twin improves interpretability and trust. • Human-in-the-loop verification suits real production data centers. | • Modest ~3-4% savings may not justify the added twin+DRL complexity. • Validated on one data center, so scaling is unproven. • Depends on good sensors and recalibration; drift could hurt safety. • Building CFD/EnergyPlus twins and many agents is compute-heavy. • Optimizes energy only - no carbon, price, or renewable signals. • Sync latency and behavior under faults aren't deeply tested. | • No carbon/renewable objective - adding it would make savings truly sustainable. • Untested at hyperscale; distributed twins and multi-agent coordination are needed. • One-shot calibration invites drift; online/transfer learning would help. • No workload or thermal forecasting for proactive control. • Only chilled-water air cooling; hybrid/liquid schemes should be added. • Safety relies on review, not formal guarantees from safe RL. • Fault tolerance and low-latency sync for transients remain open. |
| 11. Data Center Energy Evaluation Tool Development and Analysis of Power Usage Effectiveness with Different Economizer Types in Various Climate Zones (2024) | • Builds a lightweight tool to estimate data-center PUE at the design stage. • Compares economizer types (direct/indirect air-side, water-side) with and without evaporative cooling. • Computes annual PUE across many climate zones from weather and system data. • Validated against DesignBuilder/EnergyPlus dynamic simulation. • Adds sensitivity and uncertainty analysis of key parameters. • A pure engineering tool - no AI, RL, or digital twin. | • Dataset Name: ASHRAE climate-zone weather data • Source: ASHRAE standard climate zones (weather files) • URL: Not Reported • Size: Not Reported • Number of Records: Not Reported • Number of Features: Weather variables + system parameters (CRAH temp, delta-T) • Data Type: Weather / simulation input data • License: Not Reported • Purpose: Compute annual PUE across climate zones and economizer types • Preprocessing: Feed weather + system config to the tool; validated vs EnergyPlus | • Fast, low-input tool for screening many climate/economizer options early. • Accuracy close to full EnergyPlus simulation. • Covers many climate zones to guide region-appropriate design. • Quantifies concrete PUE savings from evaporative cooling. • Sensitivity/uncertainty analysis shows the key levers and risk ranges. • Practical decision support for cooling-system designers. | • Simulation only, never validated on a real data center. • Gives static annual PUE, not real-time optimization. • No AI, twin, or adaptive control. • Only air-side economizers; liquid/immersion cooling is excluded. • Wide PUE uncertainty in some zones raises reliability concerns. • Simplified load assumptions miss dynamic interactions. | • Offline design tool - a live twin would enable continuous PUE optimization. • No AI/RL to actually optimize the setpoints it analyzes. • Needs field validation and online calibration before real use. • Targets PUE only; carbon, renewables, and multi-objective goals are missing. • No workload or thermal prediction for proactive control. • Hybrid cooling (air+evaporative+liquid) isn't co-optimized. • Analysis is manual, not automated or transferable across zones. |
| 12. Energy dataset of Frontier supercomputer for waste heat recovery (2024) | • A data paper publishing one year of Frontier power and waste-heat measurements. • Uses a building-automation system with RTD sensors, a flow meter, and power meters. • Logs data over BACnet to a SQL historian, then exports to Excel. • Computes waste heat per cooling loop from temperatures, flow, and coolant properties. • Derives PUE as total facility energy over IT energy. • No model, twin, or optimizer - the contribution is the open dataset itself. | • Dataset Name: Energy dataset of Frontier supercomputer ("Frontier2023") • Source: ORNL Oak Ridge Leadership Computing Facility (Frontier) • URL: Figshare DOI 10.6084/m9.figshare.24391240 (Nature Scientific Data) • Size: 1 year; small XLSX workbook • Number of Records: ~52,560 (10-min sampling, 2023; ~5% downtime) • Number of Features: ~10+ variables - loop temps, flows, waste heat, power, PUE • Data Type: Time-series tabular (Excel XLSX) • License: Open access (Figshare, CC BY 4.0) • Purpose: Public benchmark for waste-heat-recovery and efficiency research • Preprocessing: Minimal - cleaned and documented; note the coarse 10-min sampling | • First open benchmark of real exascale power and waste-heat data. • Full-year, 10-minute data captures seasonal and daily variation. • Documents an ultra-efficient PUE ~1.05 as a reference exemplar. • Detailed sensor specs make it trustworthy and reusable. • Open Excel/Figshare format is easy to adopt. • Real world-leading system gives high external validity. | • One facility and one cooling type limits generalization. • 10-minute sampling is too coarse for fast transient control or RL. • No workload or per-rack data for fine-grained modeling. • Purely descriptive - no model, twin, or optimizer provided. • Only one year, so no ageing or multi-year trends. • Excel-with-charts format is awkward for large ML pipelines. | • No paired digital twin - building one would enable predictive thermal/heat modeling. • No AI control; the data could seed offline RL and surrogates safely. • Coarse sampling motivates higher-frequency sensing for real-time sync. • Waste-heat reuse and carbon-aware optimization are only motivated, not modeled. • No workload data to link scheduling with thermal prediction. • Single site invites federated/transfer learning across facilities. • Liquid-only, with no fault labels for fault-tolerant control research. |
| 13. Co-Design Optimization for Data Center Cooling System via Digital Twin (2026) | • A three-layer optimization of Frontier's cooling: loop partition, flow split, and setpoints. • Enumerates all 611 loop partitions and solves the continuous part with SLSQP. • Two-stage twin: a Modelica physics model plus a fast calibrated surrogate. • Minimizes annual cooling energy while keeping return temperature <= 42 C. • Steady-state supervisory control per 10-minute step, with no forecasting. • Model-based only, no RL; runs on 32 CPU cores. | • Dataset Name: Frontier 2023 operational telemetry (public release) • Source: ORNL Frontier exascale supercomputer • URL: Public ORNL Frontier release (Figshare DOI 10.6084/m9.figshare.24391240) • Size: 1 year (2023) • Number of Records: 49,353 timesteps • Number of Features: Per-CDU heat loads, total flow, supply temperatures • Data Type: Time-series tabular telemetry • License: Open access (public dataset) • Purpose: Calibrate the twin + surrogate and evaluate co-design optimization • Preprocessing: Cleaning, ASHRAE Guideline-14 calibration, surrogate fitting | • ~35% cooling savings from control/design, with no costly hardware change. • Flow-split optimization cuts design sensitivity by 93% - robust and low-cost. • Physics twin plus enumeration gives interpretable, provably optimal setpoints. • Fast surrogate makes year-long, plant-wide search practical. • Clear decision hierarchy shows where effort pays off most. | • Simulation only - never tested on the real plant. • Steady-state with no forecasting, so unfit for fast transients. • One year of fixed workloads; future load shifts aren't covered. • Lumped model can't resolve chip-level hotspots. • Energy-only on one site; no carbon, water, or cost trade-offs. • Assumes flow control that real valves may not allow. | • Offline testbed - real-time sync and drift correction are needed for a live twin. • No forecasting; predictive control would improve safety and savings. • Only energy minimized; carbon, water, and cost should be added. • No renewable or hybrid (liquid+air) cooling co-optimization. • Enumeration won't scale; safe RL could adapt online. • One site, one year; transfer/federated learning needed for hyperscale. • No fault tolerance for sensor or CDU failures. |
| 14. Transforming Future Data Center Operations and Management via Physical AI (2025) | • A "Physical AI" framework combining physics simulation, physics-informed ML, and an Omniverse twin. • Workflow: simulate, then train an ML surrogate, then RL/MPC control, then deploy and recalibrate. • Uses a neural-operator (GNOT) surrogate to predict 3D temperature fields in real time. • Ground truth comes from OpenFOAM CFD simulation. • Adds soft physics constraints to improve accuracy with little data. • Proposes a 5-tier twin (geometry to autonomous control); the control layer is mostly conceptual. | • Dataset Name: Synthetic CFD scenario dataset (authors' generation) • Source: In-house OpenFOAM CFD/HT simulator of a Singapore data hall • URL: Not Reported • Size: 500 scenarios (~340k mesh cells each) • Number of Records: 500 cases (split 400 / 50 / 50) • Number of Features: ACU supply temp + per-server power inputs -> 3D temp/velocity fields • Data Type: Synthetic CFD simulation data (3D fields) • License: Not Reported • Purpose: Train the neural-operator surrogate to predict thermal fields in real time • Preprocessing: Latin Hypercube sampling, meshing, domain decomposition, normalization | • Real-time surrogate replaces slow CFD with 0.18 C accuracy. • Physics constraints improve generalization with little data. • End-to-end platform spans geometry to actuation for hyperscale use. • The 5-tier twin gives a clear roadmap toward autonomous control. • Neural operator scales to fine meshes and arbitrary geometry. | • Only prediction is validated - no closed-loop control results. • Needs costly CFD and expert setup to generate training data. • Surrogate is geometry-specific; new layouts/liquid cooling are untested. • The RL/MPC control layer stays conceptual. • Real-time sync is described but never measured. • Sustainability (carbon, renewables) is discussed but not demonstrated. | • The strong predictor isn't yet in a validated closed-loop controller. • Air-cooled only; liquid/hybrid cooling for dense racks is needed. • CFD data cost blocks fleet-scale use; transfer learning would help. • Real-time sync (latency, drift, recalibration) is unquantified. • Carbon, water, and renewable objectives should join the control layer. • Predictions and actions need uncertainty and safety guarantees. • Fault and sensor-failure robustness is unaddressed. |
| 15. A Configurable Pythonic Data Center Model for Sustainable Cooling and ML Integration (2024) | • PyDCM, a Python library for fast data-center prototyping plus RL cooling control. • A deep RL agent sets the CRAC supply-air temperature to cut energy and carbon. • Vectorized object model (rooms to cabinets to CPUs) for fast simulation. • Uses precomputed CFD temperature gradients plus simple power curves. • Exposed as a Gymnasium environment for RL training. • The agent sees workload, weather, grid carbon, and battery state to choose setpoints. | • Dataset Name: PyDCM config + precomputed CFD/weather/carbon inputs • Source: Prior EnergyPlus prototype models + precomputed CFD + weather/grid-carbon data • URL: Open-source library (PyDCM on GitHub) • Size: Not Reported • Number of Records: Not Reported (15-min steps; 7- and 30-day episodes) • Number of Features: Workload, weather, grid carbon intensity, UPS battery SoC, CFD gradients • Data Type: Simulation environment + external time-series inputs • License: Open-source (library) • Purpose: Fast Gym environment for RL cooling control and sustainability KPIs • Preprocessing: Precompute CFD gradients, configure IT/HVAC model, vectorize | • Over 40x faster than EnergyPlus, making RL training practical. • Native Python/Gymnasium removes simulator-to-RL overhead. • Vectorized model scales with server count and is customizable. • DRL controller cuts energy and carbon and is carbon-aware. • Slightly lower resource use, plus hotspot analysis. • Open, ML-ready environment for the RL community. | • Uses precomputed (static) CFD, so it can't capture control-induced airflow changes. • Simplified physics reduces accuracy versus full CFD/EnergyPlus. • Simulation only on a small setup with modest single-digit savings. • Only DRL vs a rule-based baseline, with no MPC comparison. • Not a synchronized operational twin. • Carbon accounting depends on external data and ignores renewables/storage. | • Static CFD blocks a real-time twin - a live CFD surrogate is needed. • No forecasting; adding it would enable proactive setpoint control. • Simplified physics is unvalidated against real hyperscale data. • Single-objective - water, cost, and renewables should be added. • Only DRL vs rules; safe RL, MPC, and transfer learning are needed. • Air-only model omits liquid/hybrid cooling for dense racks. • Explainability and fault tolerance are missing for production use. |